# FORM FOR PROPOSALS ON IAPMO UPC/UMC COMMITTEE DOCUMENTS

# NOTE: All Proposals MUST be received by 5:00 PM PST on January 3, 2013.

For further information on the standards-making process, please contact the Codes and Standards Administration at 909-472-4110.

For technical assistance, please call IAPMO at 909-472-4111 or 909-230-5535.

### FOR OFFICE USE ONLY

## LOG#:  ________________

DATE REC’D: __________

# PLEASE USE SEPARATE FORM FOR EACH PROPOSAL

IAPMOʼs green initiative is to lead the organization paper free by providing the Proposed Monographs, Annual Report on Proposals and Comments in digital Adobe PDF. Note printed copies of Report on Proposals and Report on Comments will not be available at the hearings. All requested printed copies will be mailed 30 days prior to the hearing date. Please submit your request by the following dates on the request form. http://www.iapmo.org/Pages/RequestFormforROPROC.aspx

Date   December 5, 2012    	Name   Dave Cantrell                   	Tel. No.  (206) 263-8493

Company    Public Health – Seattle & King County (PHSKC)

Street Address   401 Fifth Ave, Suite #1100	 City   Seattle 	State  WA	 Zip. 98104-1818

Please Indicate Organization Represented (if any) Washington Association of Building Officials, & PHSKC

- IAPMO Document Title    Uniform Plumbing Code                IAPMO No. & Year    2012

Section/Paragraph    Chapter 17 (various sections)

- Proposal Recommends (check one): 	X  New Text	       Revised Text	 X  Deleted Text

- Proposal (Include proposed new wording, or identification of wording to be deleted):  [Note: Proposed text should be in legislative format: i.e., use underscore to denote wording to be inserted (inserted wording) and strike-through to denote wording to be deleted (deleted wording).] Please note if you are referencing a standard or other publication, please provide two copies.

1702.2 Plumbing Plan Submission. No permit for a rainwater catchment system shall be issued until complete plumbing plans, with data satisfactory to the Authority Having Jurisdiction, have been submitted and approved. No changes or connections shall be made to either the rainwater catchment or the potable water system within a site containing a rainwater catchment system without approval by the Authority Having Jurisdiction. Permit. It shall be unlawful for a person to construct, install, alter, or cause to be constructed, installed, or altered a rainwater catchment system in a building or on a premise without first obtaining a permit to do such work from the Authority Having Jurisdiction.

Exceptions:

(1) A permit is not required for exterior rainwater catchment systems used for outdoor drip and subsurface irrigation with a maximum storage capacity of 360 gallons (1363 L).

(2) A plumbing permit is not required for rainwater catchment systems for single family dwellings where outlets, piping, and system components are located on the exterior of the building. This does not exempt the need for permits where required for electrical connections, tank supports, or enclosures.

1702.3 System Changes. No changes or connections shall be made to either the rainwater catchment system or the potable water system within a site containing a rainwater catchment system requiring a permit without approval by the Authority Having Jurisdiction. System Design. Rainwater catchment systems shall be designed in accordance with this chapter by a person registered or licensed to perform plumbing design work. Components, piping, and fittings used in a rainwater catchment systems shall be listed.

Exceptions:

(1) A person registered or licensed to perform plumbing design work is not required to design rainwater catchment systems used for irrigation with a maximum storage capacity of 360 gallons (1363 L).

(2) A person registered or licensed to perform plumbing design work is not required to design rainwater catchment systems for single family dwellings where outlets, piping, and system components are located on the exterior of the building.

1702.4 Plumbing Plan Submission. No permit for a rainwater catchment system shall be issued until complete plumbing plans, with data satisfactory to the Authority Having Jurisdiction, have been submitted and approved.

1702.5 System Changes. No changes or connections shall be made to either the rainwater catchment system or the potable water system within a site containing a rainwater catchment system requiring a permit without approval by the Authority Having Jurisdiction.

1702.6 Maintenance and Inspection. Rainwater catchment systems and components shall be inspected and maintained in accordance with Section 1702.6.1 through 1702.6.3.

1702.6.1 Frequency. Rainwater catchment systems and components shall be inspected and maintained in accordance with Table 1702.6 unless more frequent inspection and maintenance is required by the manufacturer.

1702.6.2 Maintenance Log. A maintenance log for rainwater catchment systems required to have a permit in accordance with Section 1702.4 shall be maintained by the property owner and be available for inspection. The property owner or designated appointee shall ensure that a record of testing, inspection and maintenance in accordance with Table 1702.6 is maintained in the log. The log will indicate the frequency of inspection and maintenance for each system.

1702.6.3 Maintenance Responsibility. The required maintenance and inspection of rainwater catchment systems shall be the responsibility of the property owner, unless otherwise required by the Authority Having Jurisdiction.

TABLE 1702.6

RAINWATER CATCHMENT SYSTEM TESTING, INSPECTION, AND MAINTENANCE FREQUENCY

| DESCRIPTION | MINIMUM FREQUENCY |
| --- | --- |
| Inspect and clean filters and screens, and replace (where necessary). | Every 3 months |
| Inspect and verify that disinfection, filters and water quality treatment devices and systems are operational and maintaining minimum water quality requirements as determined by the Authority Having Jurisdiction. | In accordance with manufacturer’s instructions, and the Authority Having Jurisdiction |
| Inspect and clear debris from rainwater gutters, downspouts, and roof washers. | Every 6 months |
| Inspect and clear debris from roof or other above ground rainwater collection surfaces. | Every 6 months |
| Remove tree branches and vegetation overhanging roof or other aboveground rainwater collection surfaces. | As needed |
| Inspect pumps and verify operation. | After initial installation and every 12 months thereafter |
| Inspect valves and verify operation. | After initial installation and every 12 months thereafter |
| Inspect pressure tanks and verify operation. | After initial installation and every 12 months thereafter |
| Clear debris from and inspect storage tanks, locking devices, and verify operation. | After initial installation and every 12 months thereafter |
| Inspect caution labels and marking. | After initial installation and every 12 months thereafter |
| Cross-connection inspection and test* | After initial installation and every 12 months thereafter |

*The cross-connection test shall be performed in the presence of the Authority Having Jurisdiction in accordance with the requirements of this   chapter.

1702.7 Operation and Maintenance Manual. An operation maintenance manual for rainwater catchment systems required to have a permit in accordance with Section 1702.2 shall be supplied to the building owner by the system designer. The operating and maintenance manual shall include the following:

(1) Detailed diagram of the entire system and the location of system components.

(2) Instructions on operating and maintaining the system.

(3) Details on maintaining the required water quality as determined by the Authority Having Jurisdiction.

(4) Details on deactivating the system for maintenance, repair, or other purposes.

(5) Applicable testing, inspection, and maintenance frequencies in accordance with Table 1702.6.

(6) A method of contacting the manufacturer(s).

(Renumber remaining sections)

- Statement of Problem and Substantiation for Proposal:  [Note: State the problem that will be resolved by your recommendations: give the specific reason for your proposal including copies of tests, research papers, etc. If more then 200 words, it may be abstracted for publication.]

An initial printing of Chapter 16 of the 2012 Uniform Plumbing Code included a section addressing rainwater catchment systems, although these were also addressed in Chapter 17. Subsequent printings removed the technical provisions for rainwater catchment systems from Chapter 16, but did not remove the administrative provisions nor properly located them in Chapter 17. This proposed code change brings administrative provisions from Chapter 16 that were intended to apply to rainwater catchment systems and places them in Chapter 17, thus bringing both the administrative and the technical provisions into one chapter for proper code administration and enforcement. Since these provisions were already in the code, there will not be an increase to installation and enforcement of these provisions as a result of this code change. Another proposal is being submitted that removes these provisions from Chapter 16. The modifications in this proposal are as follows:

- Section 1702.2 – These provisions are relocated to the proposed new Sections 1702.4 and 1702.5, and the new wording brings the permit and permit exemption provisions from Section 1601.3 to this chapter.

- Section 1702.3 – These provisions are relocated to the new Section 1702.5, and the new wording brings the system design criteria and the exemptions from Section 1601.2 to this chapter.

- Section 1702.6 – New wording adds the maintenance and inspection provisions of Section 1601.5 that apply to rainwater catchment systems.

- Section 1702.6.1 – New wording adds the frequency of the inspection and maintenance provisions of Section 1601.5.1 that apply to rainwater catchment systems.

- Section 1702.6.2 – New wording adds the maintenance log provisions of Section 1601.5.2 that apply to rainwater catchment systems.

- Section 1702.6.3 – New wording adds the maintenance responsibility provisions of Section 1601.5.3 that apply to rainwater catchment systems.

- Table 1702.6 – New table adds testing, inspection and maintenance schedule provision of Table 1601.5 that apply to rainwater catchment systems.

- Section 1702.7 – New wording adds the operation and maintenance manual provisions of Section 1601.6 that apply to rainwater catchment systems.

- X   This Proposal is original material. [Note: Original material is considered to be the submitter's own idea based on or as a result of his/her own experience, thought or research and, to the best of his/her knowledge, is not copied from another source.)

This Proposal is not original material; its source (if known) is as follows:

I hereby grant the IAPMO all and full rights in copyright, in this proposal, and I understand that I acquire no rights in any publication of IAPMO in which this proposal in this or another similar or analogous form is used.

Signature (Required):

PLEASE USE SEPARATE FORM FOR EACH PROPOSAL  •  IAPMO FAX   •   (909) 472-4198 or (877) 852-6337

Mail to: Code Development  •  IAPMO  •  4755 E Philadelphia St  •  Ontario  •  CA  •  91761-2816

Email to: codechange@iapmo.org

INSTRUCTIONS FOR SUBMITTING PROPOSALS – PLEASE READ CAREFULLY – - Type or print in BLACK ink. - Indicate the title of the document and the document year. Also, indicate the specific section or paragraph that the proposed amendment applies to. - Check the appropriate box to indicate whether this proposal recommends adding new text, revising existing text, or deleting text. - In the space identified as “Proposal,” indicate the exact wording you propose as new or revised text, or the text you propose be deleted. - In the space titled, “Statement of Problem and Substantiation for Proposal,” state the problem that will be resolved by your recommendation and give the specific reason for your proposal. Include copies of test results, research papers, fire experience, or other materials that substantiate your recommendation. (See note below, item (f).) - Check the appropriate box to indicate whether or not this proposal is original material, and if it is not, indicate the source of the material. - Sign the proposal. If supplementary material (photographs, diagrams, reports, etc.) is included, you may be required to submit sufficient copies for all members and alternates of the technical committee. For publication in the Report on Proposals, the technical committee is authorized to abstract the “Statement of Problem and Substantiation for Proposal” if it exceeds 200 words. NOTE: The IAPMO Regulations Governing Committee Projects in Paragraph 4-3.3 state: Each proposal shall be submitted to the council secretary and shall include: (a) identification of the submitter and his or her affiliation (i.e., technical committee, organization, company), where appropriate; (b) identification of the document, edition of the document, and paragraph of the document to which the proposal is directed; (c) the proposed text of the proposal, including the wording to be added, revised (and how revised), or deleted; (d) a statement of the problem and substantiation for proposal; (e) the signature of the submitter; and (f) two copies of any document(s) (other than an IAPMO document) being proposed as a reference standard or publication (see 3-3.7).